## Slide 1: Clearlake Oaks CWD CA1710001 Lake County Jar Test
by Guy Schott, P.E.
October 21, 2022

## Slide 2: Clearlake Oaks CWD Source Water: Clear Lake Conventional Treatment

## Slide 3: Clearlake Oaks CWD.: Source Water Characteristics October 21, 2022
Source (at Pier) – After Ozonation
pH: x
Turbidity: 7.5 NTU
UVT: 80.2%
UVA: 0.095/cm
0.4 um Filtered
Turbidity: 0.29 NTU
UVT: 85.5%
UVA: 0.067/cm

## Slide 4: UVT/UVA, pathlength 10 mm
UV transmittance (UVT) is a measurement of the amount of ultraviolet light (commonly at 254 nm due to its germicidal effect) that passes through a water sample compared to the amount of light that passes through a pure water sample. The measurement is expressed as a percentage, % UVT.
%UVT = 10(-UVA) x 100%
UV absorbance (UVA) is calculated as a relative measure of the amount of light absorbed by a water sample compared with the amount of light absorbed by a pure water sample.
UVA = -log(%UVT/100)

## Slide 5: Applied Coagulants for Jar Testing (1)
NTU Technologies
Pro Pac 9800
50% Aluminum Chlorohydrate
50% Water
23.62% Al2O3
12.5% Al
83% Basicity
SG = 1.25-1.34
NSF limit: 250 mg/L as Product
10 mg/L as 9800 = Reduction 1.18 mg/L as CaCO3
Veolia Water Solutions
HYDREX 3511
Acrylamide Polymer
Low anionic polymer (dry)
NSF limit: 1.0 mg/L as Product
HYDREX 3621
Acrylamide Polymer
Cationic polymer (dry)
NSF limit: 1.0 mg/L as Product

## Slide 6: Applied Coagulants for Jar Testing (2)
NTU Technologies
Pro Pac 9810
45-50% Aluminum Chlorohydrate
45-50% Water
~22.4% Al2O3
~11.9% Al
83% Basicity
5% polyamine (50% water, 50% active polyamines)
SG = 1.25-1.34
NSF limit: 200 mg/L as Product;
Product dose 40 mg/L = 1 mg/L polyamines active
NTU Technologies
AD313P
Acrylamide Polymer
Anionic polymer (dry)
NSF limit: 1.0 mg/L as Product
NTU Technologies
CD313P
Acrylamide Polymer
Cationic polymer (dry)
NSF limit: 1.0 mg/L as Product

## Slide 7: Coagulant Information
Unless stated otherwise, all coagulant doses are reported as Product (100% strength).
Preparation of coagulant stock solutions are generally 1.0 and/or 0.1 percent strength using 100 and/or 200 mL volumetric flasks.
Finnpipette F2 variable volume pipette, capacity 100-1000 micro liters is used for stock solution preparation and coagulant aid jar test dosing.
Finnpipette F2 variable volume pipette, capacity 0.5-5 mL is used for primary coagulant jar test dosing.

## Slide 8: Source: Clear Lake (Pier): Jar Test 1-8 Results Flash 2 min (200 RPM), Floc1 2 min (110 RPM), Floc2 2 min (60 RPM)
Jar # | O3 applied | 9800 mg/L | Ballast Sand 110 um | HYDREX 3511 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 5 min
J1 | Yes | 100 | 1 tsp | 0.7 | 0.11 | 89.9 | 0.046 | 31.3 | 0.83
J2 | Yes | 110 | 1 tsp | 0.7 | 0.18 | 89.9 | 0.046 | 31.3 | 0.79
J3 | Yes | 120 | 1 tsp | 0.7 | 0.19 | 89.7 | 0.047 | 29.9 | 0.81
J4 | Yes | 130 | 1 tsp | 0.7 | 0.13 | - | - | - | 0.89
J5 | Yes | 80 | 1 tsp | 0.7 | 0.28 | 89.2 | 0.049 | 26.9 | 1.07
J6 | Yes | 90 | 1 tsp | 0.7 | 0.30 | 89.1 | 0.049 | 26.9 | 1.20
J7 | Yes | 160 | 1 tsp | 0.7 | 0.09 | 90.8 | 0.041 | 38.8 | 0.47
J8 | Yes | 170 | 1 tsp | 0.7 | 0.08 | 90.9 | 0.040 | 40.3 | 0.31

## Slide 9: Source: Clear Lake (Pier): Jar Test 9-16 Results Flash 2 min (200 RPM), Floc1 2 min (110 RPM), Floc2 2 min (60 RPM)
Jar # | O3 applied | 9800 mg/L | Ballast Sand 110 um | HYDREX 3511 mg/L | HYDREX 3621 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 5 min
J9 | Yes | 120 | 1 tsp | 0.3 | - | 0.19 | 89.7 | 0.047 | 29.9 | 1.40
J10 | Yes | 120 | 1 tsp | 0.4 | - | 0.21 | 89.6 | 0.047 | 29.9 | 1.31
J11 | Yes | 120 | 1 tsp | 0.5 | - | 0.18 | 89.6 | 0.047 | 29.9 | 1.05
J12 | Yes | 120 | 1 tsp | 0.7 | - | 0.16 | 89.8 | 0.046 | 31.3 | 1.00
J13 | Yes | 120 | 1 tsp | 0.4 | - | 0.11 | 89.8 | 0.046 | 31.3 | 1.00
J14 | Yes | 120 | 1 tsp | 0.7 | - | 0.12 | 90.0 | 0.045 | 32.8 | 0.98
J15 | Yes | 120 | 1 tsp | - | 0.4 | 0.06 | 89.9 | 0.046 | 31.3 | 0.59
J16 | Yes | 120 | 1 tsp | - | 0.7 | 0.06 | 90.3 | 0.044 | 34.3 | 0.49

## Slide 10: Source: Clear Lake (Pier): Jar Test 17-24 Results Flash 20 sec (200 RPM), Floc 5 min (30 RPM)
Jar # | O3 applied | 9810 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J17 | Yes | 90 | 0.08 | 90.0 | 0.045 | 32.8 | 0.50
J18 | Yes | 100 | 0.05 | 90.4 | 0.043 | 35.8 | 0.46
J19 | Yes | 110 | 0.06 | 90.6 | 0.042 | 37.3 | 0.35
J20 | Yes | 120 | 0.06 | 90.6 | 0.042 | 37.3 | 0.33
J21 | Yes | 100 | 0.06 | 90.5 | 0.043 | 35.8 | 0.33
J22 | Yes | 110 | 0.05 | 90.3 | 0.044 | 34.3 | 0.32
J23 | Yes | 120 | 0.05 | 90.4 | 0.043 | 35.8 | 0.38
J24 | Yes | 130 | 0.05 | 90.6 | 0.042 | 37.3 | 0.31

## Slide 11: Source: Clear Lake (Pier): Jar Test 25-28 Results Flash 2 min (200 RPM), Floc1 2 min (110 RPM), Floc2 2 min (60 RPM)
Jar # | O3 applied | 9800 mg/L | Ballast Sand 110 um | HYDREX 3511 mg/L | HYDREX 3611 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 5 min
J25 | Yes | 120 | 1 tsp | 0.4 | - | 0.12 | 90.1 | 0.045 | 32.8 | 1.03
J26 | Yes | 120 | 1 tsp | 0.7 | - | 0.15 | 89.9 | 0046 | 31.3 | 0.84
J27 | Yes | 120 | 1 tsp | - | 0.4 | 0.06 | 90.3 | 0.044 | 34.3 | 0.86
J28 | Yes | 120 | 1 tsp | - | 0.7 | 0.06 | 90.2 | 0.044 | 34.3 | 0.66

## Slide 12: Source: Clear Lake (Pier): Jar Test 29-36 Results Flash 2 min (200 RPM), Floc1 2 min (110 RPM), Floc2 2 min (60 RPM)
Jar # | O3 applied | 9800 mg/L | Ballast Sand 110 um | AD313P mg/L | CD313P mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 5 min
J29 | Yes | 120 | 1 tsp | 0.15 | - | 0.17 | 90.1 | 0.045 | 32.8 | 0.79
J30 | Yes | 120 | 1 tsp | 0.25 | - | 0.18 | 90.4 | 0.043 | 35.8 | 0.69
J31 | Yes | 120 | 1 tsp | 0.40 | - | 0.13 | 90.2 | 0.044 | 34.3 | 0.66
J32 | Yes | 120 | 1 tsp | 0.50 | - | 0.07 | 90.5 | 0.043 | 35.8 | 0.45
J33 | Yes | 120 | 1 tsp | - | 0.15 | 0.06 | 90.3 | 0.044 | 34.3 | 0.82
J34 | Yes | 120 | 1 tsp | - | 0.25 | 0.06 | 90.1 | 0.045 | 32.8 | 0.76
J35 | Yes | 120 | 1 tsp | - | 0.40 | 0.06 | 90.2 | 0.044 | 34.3 | 0.63
J36 | Yes | 120 | 1 tsp | - | 0.50 | 0.06 | 90.2 | 0.044 | 34.3 | 0.58

## Slide 13: Source: Clear Lake (Pier): Jar Test 37-40 Results Flash 2 min (200 RPM), Floc1 2 min (110 RPM), Floc2 2 min (60 RPM) Pre-ozone was applied
Jar # | 9800 mg/L | Ballast Sand 110 um | HYDREX 3511 mg/L | HYDREX 3611 mg/L | AD313P mg/L | CD313P mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 5 min
J37 | 120 | 1 tsp | 0.5 | - | - | - | 0.10 | 90.0 | 0.045 | 32.8 | 0.75
J38 | 120 | 1 tsp | - | 0.5 | - | - | 0.09 | 89.9 | 0.046 | 31.3 | 0.89
J39 | 120 | 1 tsp | - | - | 0.5 | - | 0.14 | 89.9 | 0.046 | 31.3 | 0.74
J40 | 120 | 1 tsp | - | - | - | 0.5 | 0.06 | 90.4 | 0.043 | 35.8 | 0.52

## Slide 14: Source: Clear Lake (Pier): Jar Test 41-44 Results Flash 2 min (200 RPM), Floc1 2 min (110 RPM), Floc2 2 min (60 RPM) Pre-ozone was applied
Jar # | 9810 mg/L | Ballast Sand 110 um | HYDREX 3511 mg/L | HYDREX 3611 mg/L | AD313P mg/L | CD313P mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 5 min
J41 | 120 | 1 tsp | 0.5 | - | - | - | 0.16 | 90.4 | 0.043 | 35.8 | 1.50
J42 | 120 | 1 tsp | - | 0.5 | - | - | 0.08 | 89.7 | 0.047 | 29.9 | 1.36
J43 | 120 | 1 tsp | - | - | 0.5 | - | 0.08 | 90.0 | 0.045 | 32.8 | 1.37
J44 | 120 | 1 tsp | - | - | - | 0.5 | 0.07 | 89.9 | 0.046 | 31.3 | 0.94

## Slide 15: Jar Testing – Procedures for Actiflo, 1-Liter Jars
Fill jars with source water prior to coagulant injection and set paddle speed at 30 rpm
Add chemicals (i.e., NaOCl, primary coagulant, coagulant aid) to each jar
Jars 1 – 20 (Actiflow only): Start flash mix and hold for 2 minutes (200 rpm)
Add ballast sand and acrylamide polymer during flash mixing
Reduce paddled speed to 110 RPM for 2 minutes
For Jars 21 – 44 (Actiflow only): Flash 200 for 20 sec, then reduce paddle speed to 110 and add sand/polymer
Reduce paddle speed to 60 RPM for 2 minutes
Raise paddles out of water and settled for 1 minute
Syringe 25 mL from each jar taken 1-inch below surface (25 mL/12 sec rate)
Filtered through 1.2 um isopore membrane into cuvette (drip rate, 15 mL/90 sec)
Measure filtrate turbidity, chlorine residual and %UVT or UVA
Measure settled water turbidity after 5 minutes of total setting
Record all data

## Slide 16: Jar Test Filterability Test Equipment
Turbidity Instrument
Syringe w/Luer-Lock Tip, 30 cc
(part#: 2225800, by Hach)
Swinnex Filter Holder, 25 mm (part#: SX0002500)
Isopore Membrane Filter, 1.2 um absolute
pore size,
Φ= 25 mm , thickness: 24 um,
hydrophilic polycarbonate membrane
(part #: RTTP02500)
Go to Sigma-Aldrich for laboratory supplies http://www.sigmaaldrich.com/united-states.html

## Slide 17: Isopore Membrane Information
Categories | Information
trade name | Isopore
filter color | White
chemistry | Polycarbonate (PC)
water flow rate | Avg. 175 mL/min x cm² (typical results @ 10 psi)
media | Isopore®
wettability | Hydrophilic
porosity | 14.7%
pore size | 1.2 µm
bubble point at 23 °C | 1.0 bar, air with water
thickness | 24 µm
filter diameter (ø) | 25 mm
material size | polycarbonate, Hydrophilic, 1.2 µm, 25 mm, white, plain, 100

## Slide 18: Isopore Membrane Background Information
The Isopore membrane is a polycarbonate, track-etched screen filter recommended for all analyses in which the sample is viewed on the surface of the membrane. The Isopore membrane is composed of polycarbonate film, which has a smooth, glass-like surface for clearer sample observation. The unique manufacturing process of the membrane ensures a precise pore diameter and a consistent pore size for accurate separation of samples by size. Matched-weight filters are not usually required because of low, constant tar and ash weights. Features & Benefits: Membrane structure retains particles on the surface, simplifying counting and analysis

## Slide 19: Jar Test - Filterability Test
Syringe ~ 25 mL from jar (after 5-minutes of settling)
Filter-to-waste 3-5 mL
Filter directly into clean cuvette
Measure turbidity
Note: Take several readings before recording final NTU results. Micro bubbles can adhere to glass causing false NTU readings. To remove bubbles, tilt cuvette up to 90 degrees.

## Slide 20: Contact
Guy Schott, P.E.
State Water Resources Control Board
Division of Drinking Water
Santa Rosa, CA
Go to Stock Solution/Dose calculations/Jar Test Results for tools to download
www.waterboards.ca.gov/drinking_water/programs/districts/mendocino_district.html
Email: Guy Schott - Guy.Schott@waterboards.ca.gov
Office Number: 707-576-2732