## Slide 1: City of American Canyon CA2810005, Napa County, Jar Test
by Guy Schott, P.E. June 20, 2022

## Slide 2: Source – North Bay Aqueduct

## Slide 3: Conventional and Membrane Treatment Plants

## Slide 4: City of American Canyon Source & Treated Water Characteristics, June 20, 2022
Source – North Bay Aqueduct
pH: 7.70 – 7.92
Alkalinity: 81 mg/L as CaCO3
Turbidity: 9.06 NTU
UVT: 63.7%,
UVA: 0.195/cm
0.4 um Filtered
Turbidity: 0.42 NTU
UVT: 72.4%,
UVA: 0.139/cm
Plant Settled Water
1.0 NTU
Plant Filtrate Water
0.07 NTU
UVT: 92.3%,
UVA: 0.034/cm
Plant Filtrate Post Chlorine Water
0.08 NTU
UVT: 94.1%,
UVA: 0.026/cm

## Slide 5: Applied Coagulants for Jar Testing (1)
7% Acid Alum
36.48% Alum
3.25% Al
6.2% Al2O3
7% H2SO4
SG = 1.30
NSF limit: 450 mg/L as Product
Chemtrade
10 mg/L as Alum = Reduction 6.99 mg/L as CaCO3 with H2SO4
Nalclear 8170 Pulv
Polyacrylamide
NSF limit: 1 mg/L as Product

## Slide 6: Applied Coagulants for Jar Testing (2)
Pro Pac 9800 (NTU Technologies)
50% Aluminum Chlorohydrate
50% Water
23.62% Al2O3
12.5% Al
83% Basicity
SG = 1.25-1.34
NSF limit: 250 mg/L as Product
10 mg/L as 9800 = Reduction 1.18 mg/L as CaCO3
Pro Pac 9890 (NTU Technologies)
35-45% Aluminum Chlorohydrate
20% polyamine (50% water, 50% active polyamines)
35-45% Water
~18.9% Al2O3
~10.5% Al
83% Basicity
SG = 1.25-1.34
NSF limit: 50 mg/L as Product;
Product dose 10 mg/L = 1 mg/L polyamines active

## Slide 7: UVT/UVA, pathlength 10 mm
UV transmittance (UVT) is a measurement of the amount of ultraviolet light (254 nm) that passes through a water sample compared to the amount of light that passes through a pure water sample. The measurement is expressed as % UVT.
%UVT = 10(-UVA) x 100%
UV absorbance (UVA) is calculated as a relative measure of the amount of light absorbed by a water sample compared with the amount of light absorbed by a pure water sample.
UVA = -log(%UVT/100)

## Slide 8: Laboratory Charge Analyzer
LCA: Used to determine coagulant demand of a source water entering the treatment plant.
Source pH: 7.74-7.90
LCA #1: 7% Acid Alum
pH adjusted to 6.6 w/acidic acid
Alum: 37 mg/L as Alum
H2SO4: 7.1 mg/L
LCA #2: 9800
No pH adjustment
44.0 mg/L as product

## Slide 9: Coagulant Information
Unless stated otherwise, all coagulant doses are reported as Product (100% strength).
Aluminum Sulfate doses are reported as hydrated Al2(SO4)3*14.3H20.
Preparation of coagulant stock solutions are generally 1.0 and/or 0.1 percent strength using 100 and/or 200 mL volumetric flasks.
Finnpipette F2 variable volume pipette, capacity 100-1000 micro liters is used for stock solution preparation and coagulant aid jar test dosing.
Finnpipette F2 variable volume pipette, capacity 0.5-5 mL is used for primary coagulant jar test dosing.

## Slide 10: American Canyon: Source: North Bay Aqueduct Summary of Optimum Dose/Coagulants for Filtrate Jars
Jar# | Alum Al2(SO4)3*14.3H20 mg/L | H2SO4 mg/L | 9800 mg/L | Alkalinity Reduction mg/L as CaCO3 | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
A | 0 | 0 | 75 | 8.87 | 0.04 | 92.5 | 0.033 | 76.3 | 0.57
B | 0 | 0 | 80 | 9.46 | 0.04 | 92.7 | 0.032 | 77.0 | 0.44
C | 80 | 15.4 | 0 | 55.9 | 0.04 | 92.1 | 0.035 | 74.8 | 1.10
D | 85 | 16.3 | 0 | 59.4 | 0.04 | 92.2 | 0.034 | 75.5 | 0.96

## Slide 11: American Canyon; Jar Test 1 - 8 Results Flash Mix 200 RPM (20 sec); Floc Mix 30 RPM (5 min)
Jar# | Alum Al2(SO4)3*14.3H20 mg/L | H2SO4 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J1 | 35 | 6.7 | 0.10 | 87.9 | 0.055 | 60.4 | 3.66
J2 | 40 | 7.7 | 0.11 | 88.5 | 0.052 | 62.6 | 2.66
J3 | 45 | 8.6 | 0.18 | 89.1 | 0.049 | 64.7 | 2.46
J4 | 50 | 9.6 | 0.06 | 90.7 | 0.042 | 69.8 | 1.47
J5 | 55 | 10.6 | 0.07 | 90.8 | 0.041 | 70.5 | 1.84
J6 | 60 | 11.5 | 0.07 | 91.2 | 0.039 | 71.9 | 1.99
J7 | 65 | 12.5 | 0.05 | 91.7 | 0.037 | 73.4 | 1.79
J8 | 70 | 13.4 | 0.05 | 92.4 | 0.035 | 74.8 | 1.77

## Slide 12: American Canyon; Jar Test 9 - 16 Results Flash Mix 200 RPM (20 sec); Floc Mix 30 RPM (5 min)
Jar# | Alum Al2(SO4)3*14.3H20 mg/L | H2SO4 mg/L | 8170 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J9 | 75 | 14.4 | 0 | 0.04 | 92.4 | 0.034 | 75.5 | 1.55
J10 | 80 | 15.4 | 0 | 0.08 | 92.7 | 0.032 | 77.0 | 1.74
J11 | 85 | 16.3 | 0 | 0.04 | 92.8 | 0.032 | 77.0 | 1.93
J12 | 90 | 17.3 | 0 | 0.04 | 92.8 | 0.032 | 77.0 | 2.12
J13 | 80 | 15.4 | 0 | 0.04 | 92.7 | 0.032 | 77.0 | 1.42
J14 | 80 | 15.4 | 0.2 | 0.04 | 92.6 | 0.033 | 76.3 | 1.64
J15 | 80 | 15.4 | 0.25 | 0.04 | 92.6 | 0.033 | 76.3 | 1.84
J16 | 80 | 15.4 | 0.3 | 0.05 | 92.5 | 0.033 | 76.3 | 1.68

## Slide 13: American Canyon; Jar Test 17 - 20 Results Flash Mix 200 RPM (20 sec); Floc Mix 30 RPM (5 min)
Jar# | 9800 mg/L | 9890 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J17 | 55 | 0 | 0.04 | 91.3 | 0.039 | 71.9 | 1.08
J18 | 60 | 0 | 0.04 | 91.5 | 0.038 | 72.7 | 1.32
J19 | 55 | 3 | 0.04 | 91.8 | 0.037 | 73.4 | 1.21
J20 | 60 | 3 | 0.04 | 91.9 | 0.036 | 74.1 | 1.25

## Slide 14: American Canyon; Jar Test 21 - 24 Results Flash Mix 200 RPM (20 sec); Floc Mix 30 RPM (5 min)
Jar# | Alum Al2(SO4)3*14.3H20 mg/L | H2SO4 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J21 | 50 | 9.6 | 0.06 | 90.1 | 0.045 | 67.6 | 1.77
J22 | 60 | 11.5 | 0.05 | 90.9 | 0.041 | 70.5 | 1.66
J23 | 70 | 13.4 | 0.05 | 91.2 | 0.039 | 71.9 | 1.72
J24 | 80 | 15.4 | 0.05 | 92.3 | 0.034 | 75.5 | 1.17

## Slide 15: American Canyon; Jar Test 25 - 32 Results Flash Mix 200 RPM (20 sec); Floc Mix 30 RPM (5 min)
Jar# | Alum Al2(SO4)3*14.3H20 mg/L | H2SO4 mg/L | 9800 mg/L | Filtrate NTU | Filtrate %UVT | Filtrate UVA/cm | %UVA Reduction | Settle NTU 25 min
J25 | 0 | 0 | 60 | 0.05 | 91.5 | 0.038 | 72.7 | 0.41
J26 | 0 | 0 | 65 | 0.04 | 92.0 | 0.036 | 74.1 | 0.49
J27 | 0 | 0 | 70 | 0.04 | 92.3 | 0.034 | 75.5 | 0.45
J28 | 0 | 0 | 75 | 0.04 | 92.6 | 0.033 | 76.3 | 0.43
J29 | 0 | 0 | 75 | 0.04 | 92.5 | 0.033 | 76.3 | 0.57
J30 | 0 | 0 | 80 | 0.04 | 92.7 | 0.032 | 77.0 | 0.44
J31 | 80 | 15.4 | 0 | 0.04 | 92.1 | 0.035 | 74.8 | 1.10
J32 | 85 | 16.3 | 0 | 0.04 | 92.2 | 0.034 | 75.5 | 0.96

## Slide 16: Jars 1-4 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulant 7% Acid Alum

## Slide 17: Jars 1-4: End of 5-minute flocculation (30 RPM) duration.
35 mg/L Alum
6.7 mg/L H2SO4
Filtrate: 0.10 NTU
UVT: 87.9%
UVA: 0.055/cm
UVA Reduction: 60.4%
Settled: 3.66 NTU
40 mg/L Alum
7.7 mg/L H2SO4
Filtrate: 0.11 NTU
UVT: 88.5%
UVA: 0.052/cm
UVA Reduction: 62.6%
Settled: 2.66 NTU
45 mg/L Alum
8.6 mg/L H2SO4
Filtrate: 0.18 NTU
UVT: 89.1%
UVA: 0.049/cm
UVA Reduction: 64.7%
Settled: 2.46 NTU
50 mg/L Alum
9.6 mg/L H2SO4
Filtrate: 0.06 NTU
UVT: 90.7%
UVA: 0.049/cm
UVA Reduction: 69.8%
Settled: 1.47NTU

## Slide 18: Jars 1-4: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 19: Jars 1-4: After 25-minutes of settling, settled water turbidity is taken.
35 mg/L Alum
6.7 mg/L H2SO4
Filtrate: 0.10 NTU
UVT: 87.9%
UVA: 0.055/cm
UVA Reduction: 60.4%
Settled: 3.66 NTU
40 mg/L Alum
7.7 mg/L H2SO4
Filtrate: 0.11 NTU
UVT: 88.5%
UVA: 0.052/cm
UVA Reduction: 62.6%
Settled: 2.66 NTU
45 mg/L Alum
8.6 mg/L H2SO4
Filtrate: 0.18 NTU
UVT: 89.1%
UVA: 0.049/cm
UVA Reduction: 64.7%
Settled: 2.46 NTU
50 mg/L Alum
9.6 mg/L H2SO4
Filtrate: 0.06 NTU
UVT: 90.7%
UVA: 0.049/cm
UVA Reduction: 69.8%
Settled: 1.47NTU

## Slide 20: Jars 5-8 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulant 7% Acid Alum

## Slide 21: Jars 5-8: End of 5-minute flocculation (30 RPM) duration.
55 mg/L Alum
10.6 mg/L H2SO4
Filtrate: 0.07 NTU
UVT: 90.8%
UVA: 0.041/cm
UVA Reduction: 70.5%
Settled: 1.84 NTU
60 mg/L Alum
11.5 mg/L H2SO4
Filtrate: 0.07 NTU
UVT: 91.2%
UVA: 0.039/cm
UVA Reduction: 71.9%
Settled: 1.99 NTU
65 mg/L Alum
12.5 mg/L H2SO4
Filtrate: 0.05 NTU
UVT: 91.7%
UVA: 0.037/cm
UVA Reduction: 73.4%
Settled: 1.79 NTU
70 mg/L Alum
13.4 mg/L H2SO4
Filtrate: 0.05 NTU
UVT: 91.7%
UVA: 0.035/cm
UVA Reduction: 74.8%
Settled: 1.77 NTU

## Slide 22: Jars 5-8: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 23: Jars 5-8: After 25-minutes of settling, settled water turbidity is taken.
55 mg/L Alum
10.6 mg/L H2SO4
Filtrate: 0.07 NTU
UVT: 90.8%
UVA: 0.041/cm
UVA Reduction: 70.5%
Settled: 1.84 NTU
60 mg/L Alum
11.5 mg/L H2SO4
Filtrate: 0.07 NTU
UVT: 91.2%
UVA: 0.039/cm
UVA Reduction: 71.9%
Settled: 1.99 NTU
65 mg/L Alum
12.5 mg/L H2SO4
Filtrate: 0.05 NTU
UVT: 91.7%
UVA: 0.037/cm
UVA Reduction: 73.4%
Settled: 1.79 NTU
70 mg/L Alum
13.4 mg/L H2SO4
Filtrate: 0.05 NTU
UVT: 91.7%
UVA: 0.035/cm
UVA Reduction: 74.8%
Settled: 1.77 NTU

## Slide 24: Jars 9-12 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulant 7% Acid Alum

## Slide 25: Jars 9-12: End of 5-minute flocculation (30 RPM) duration.
75 mg/L Alum
14.4 mg/L H2SO4
Filtrate: 0.04 NTU
UVT: 92.4%
UVA: 0.034/cm
UVA Reduction: 75.5%
Settled: 1.55 NTU
80 mg/L Alum
15.4 mg/L H2SO4
Filtrate: 0.08 NTU
UVT: 92.7%
UVA: 0.032/cm
UVA Reduction: 77.0%
Settled: 1.74 NTU
85 mg/L Alum
16.3 mg/L H2SO4
Filtrate: 0.04 NTU
UVT: 92.8%
UVA: 0.032/cm
UVA Reduction: 77.0%
Settled: 1.93 NTU
90 mg/L Alum
17.3 mg/L H2SO4
Filtrate: 0.04 NTU
UVT: 92.8%
UVA: 0.032/cm
UVA Reduction: 77.0%
Settled: 2.12 NTU

## Slide 26: Jars 9-12: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 27: Jars 9-12: After 25-minutes of settling, settled water turbidity is taken.
75 mg/L Alum
14.4 mg/L H2SO4
Filtrate: 0.04 NTU
UVT: 92.4%
UVA: 0.034/cm
UVA Reduction: 75.5%
Settled: 1.55 NTU
80 mg/L Alum
15.4 mg/L H2SO4
Filtrate: 0.08 NTU
UVT: 92.7%
UVA: 0.032/cm
UVA Reduction: 77.0%
Settled: 1.74 NTU
85 mg/L Alum
16.3 mg/L H2SO4
Filtrate: 0.04 NTU
UVT: 92.8%
UVA: 0.032/cm
UVA Reduction: 77.0%
Settled: 1.93 NTU
90 mg/L Alum
17.3 mg/L H2SO4
Filtrate: 0.04 NTU
UVT: 92.8%
UVA: 0.032/cm
UVA Reduction: 77.0%
Settled: 2.12 NTU

## Slide 28: Jars 13-16 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulants 7% Acid Alum/8170

## Slide 29: Jars 13-16: End of 5-minute flocculation (30 RPM) duration.
80 mg/L Alum
15.4 mg/L H2SO4
0 mg/L 8170
Filtrate: 0.04 NTU
UVT: 92.7%
UVA: 0.032/cm
UVA Reduction: 77.0%
Settled: 1.42 NTU
80 mg/L Alum
15.4 mg/L H2SO4
0.2 mg/L 8170
Filtrate: 0.04 NTU
UVT: 92.6%
UVA: 0.033/cm
UVA Reduction: 76.3%
Settled: 1.64 NTU
80 mg/L Alum
15.4 mg/L H2SO4
0.25 mg/L 8170
Filtrate: 0.04 NTU
UVT: 92.6%
UVA: 0.033/cm
UVA Reduction: 76.3%
Settled: 1.84 NTU
80 mg/L Alum
15.4 mg/L H2SO4
0.3 mg/L 8170
Filtrate: 0.05 NTU
UVT: 92.5%
UVA: 0.033/cm
UVA Reduction: 76.3%
Settled: 1.68 NTU

## Slide 30: Jars 13-16: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 31: Jars 13-16: After 25-minutes of settling, settled water turbidity is taken.
80 mg/L Alum
15.4 mg/L H2SO4
0 mg/L 8170
Filtrate: 0.04 NTU
UVT: 92.7%
UVA: 0.032/cm
UVA Reduction: 77.0%
Settled: 1.42 NTU
80 mg/L Alum
15.4 mg/L H2SO4
0.2 mg/L 8170
Filtrate: 0.04 NTU
UVT: 92.6%
UVA: 0.033/cm
UVA Reduction: 76.3%
Settled: 1.64 NTU
80 mg/L Alum
15.4 mg/L H2SO4
0.25 mg/L 8170
Filtrate: 0.04 NTU
UVT: 92.6%
UVA: 0.033/cm
UVA Reduction: 76.3%
Settled: 1.84 NTU
80 mg/L Alum
15.4 mg/L H2SO4
0.3 mg/L 8170
Filtrate: 0.05 NTU
UVT: 92.5%
UVA: 0.033/cm
UVA Reduction: 76.3%
Settled: 1.68 NTU

## Slide 32: Jars 17-20 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulants 9800/9890

## Slide 33: Jars 17-20: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.
55 mg/L 9800
0 mg/L 9890
Filtrate: 0.04 NTU
UVT: 91.3%
UVA: 0.039/cm
UVA Reduction: 71.9%
Settled: 1.08 NTU
60 mg/L 9800
0 mg/L 9890
Filtrate: 0.04 NTU
UVT: 91.5%
UVA: 0.038/cm
UVA Reduction: 72.7%
Settled: 1.32 NTU
60 mg/L 9800
3 mg/L 9890
Filtrate: 0.04 NTU
UVT: 91.9%
UVA: 0.036/cm
UVA Reduction: 74.1%
Settled: 1.25 NTU
55 mg/L 9800
3 mg/L 9890
Filtrate: 0.04 NTU
UVT: 91.8%
UVA: 0.037/cm
UVA Reduction: 73.4%
Settled: 1.21 NTU

## Slide 34: Jars 17-20: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 35: Jars 17-20: After 25-minutes of settling, settled water turbidity is taken.
55 mg/L 9800
0 mg/L 9890
Filtrate: 0.04 NTU
UVT: 91.3%
UVA: 0.039/cm
UVA Reduction: 71.9%
Settled: 1.08 NTU
60 mg/L 9800
0 mg/L 9890
Filtrate: 0.04 NTU
UVT: 91.5%
UVA: 0.038/cm
UVA Reduction: 72.7%
Settled: 1.32 NTU
60 mg/L 9800
3 mg/L 9890
Filtrate: 0.04 NTU
UVT: 91.9%
UVA: 0.036/cm
UVA Reduction: 74.1%
Settled: 1.25 NTU
55 mg/L 9800
3 mg/L 9890
Filtrate: 0.04 NTU
UVT: 91.8%
UVA: 0.037/cm
UVA Reduction: 73.4%
Settled: 1.21 NTU

## Slide 36: Jars 21-24 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (30 RPM) Pictures not Available Applied Coagulant 7% Acid Alum

## Slide 37: Jars 25-28 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulant 9800

## Slide 38: Jars 25-28: End of 5-minute flocculation (30 RPM) duration.
60 mg/L 9800
Filtrate: 0.05 NTU
UVT: 91.5%
UVA: 0.038/cm
UVA Reduction: 72.7%
Settled: 0.41 NTU
65 mg/L 9800
Filtrate: 0.04 NTU
UVT: 92.0%
UVA: 0.036/cm
UVA Reduction: 74.1%
Settled: 0.49 NTU
70 mg/L 9800
Filtrate: 0.04 NTU
UVT: 92.3%
UVA: 0.034/cm
UVA Reduction: 75.5%
Settled: 0.45 NTU
75 mg/L 9800
Filtrate: 0.04 NTU
UVT: 92.6%
UVA: 0.033/cm
UVA Reduction: 76.3%
Settled: 0.45 NTU

## Slide 39: Jars 25-28: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 40: Jars 25-28: After 25-minutes of settling, settled water turbidity is taken.
60 mg/L 9800
Filtrate: 0.05 NTU
UVT: 91.5%
UVA: 0.038/cm
UVA Reduction: 72.7%
Settled: 0.41 NTU
65 mg/L 9800
Filtrate: 0.04 NTU
UVT: 92.0%
UVA: 0.036/cm
UVA Reduction: 74.1%
Settled: 0.49 NTU
70 mg/L 9800
Filtrate: 0.04 NTU
UVT: 92.3%
UVA: 0.034/cm
UVA Reduction: 75.5%
Settled: 0.45 NTU
75 mg/L 9800
Filtrate: 0.04 NTU
UVT: 92.6%
UVA: 0.033/cm
UVA Reduction: 76.3%
Settled: 0.45 NTU

## Slide 41: Jars 29-32 Test Flash Mix 20 Sec (200 RPM) Floc Mix 5 min (30 RPM) Applied Coagulants 7% Acid Alum/9800

## Slide 42: Jars 29-32: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.
80 mg/L Alum
15.4 mg/L H2SO4
Filtrate: 0.04 NTU
UVT: 92.1%
UVA: 0.035/cm
UVA Reduction: 74.8%
Settled: 1.60 NTU
80 mg/L 9800
Filtrate: 0.04 NTU
UVT: 92.7%
UVA: 0.032/cm
UVA Reduction: 77.0%
Settled: 0.44 NTU
75 mg/L 9800
Filtrate: 0.04 NTU
UVT: 92.5%
UVA: 0.033/cm
UVA Reduction: 76.3%
Settled: 0.57 NTU
85 mg/L Alum
16.3 mg/L H2SO4
Filtrate: 0.04 NTU
UVT: 92.2%
UVA: 0.034/cm
UVA Reduction: 75.5%
Settled: 0.96 NTU

## Slide 43: Jars 29-32: After 5 min of settling, 25 mL is syringed for filterability and %UVT/UVA.

## Slide 44: Jars 29-32: After 25-minutes of settling, settled water turbidity is taken.
80 mg/L Alum
15.4 mg/L H2SO4
Filtrate: 0.04 NTU
UVT: 92.1%
UVA: 0.035/cm
UVA Reduction: 74.8%
Settled: 1.60 NTU
80 mg/L 9800
Filtrate: 0.04 NTU
UVT: 92.7%
UVA: 0.032/cm
UVA Reduction: 77.0%
Settled: 0.44 NTU
75 mg/L 9800
Filtrate: 0.04 NTU
UVT: 92.5%
UVA: 0.033/cm
UVA Reduction: 76.3%
Settled: 0.57 NTU
85 mg/L Alum
16.3 mg/L H2SO4
Filtrate: 0.04 NTU
UVT: 92.2%
UVA: 0.034/cm
UVA Reduction: 75.5%
Settled: 0.96 NTU

## Slide 45: Jar Testing for 1-Liter Jars: Procedures for Most Treatment Plants
Fill jars with source water prior to coagulant injection and set paddle speed at 30 rpm
Add chemicals (i.e., NaOCl, primary coagulant, coagulant aid) to each jar
Flash mix for 15-30 seconds (200 rpm)
Slow mix for 5 minutes (20-30 rpm)
Settled for 5 minutes. Syringe 25 mL from each jar taken 1-inch below surface (25 mL/12 sec rate)
Filtered through 1.2 um isopore membrane into cuvette drip rate, 15 mL/(50-90 sec)
Measure filtrate turbidity, chlorine residual and %UVT/UVA
Measure settled water turbidity after 25 minutes of total setting
Record all data

## Slide 46: Jar Test Filterability Test Equipment
Turbidity Instrument
Syringe w/Luer-Lock Tip, 30 cc
(part#: 2225800, by Hach)
Swinnex Filter Holder, 25 mm (part#: SX0002500)
Isopore Membrane Filter, 1.2 um absolute
pore size,
Φ= 25 mm , thickness: 24 um,
hydrophilic polycarbonate membrane
(part #: RTTP02500)
Go to Sigma-Aldrich for laboratory supplies http://www.sigmaaldrich.com/united-states.html

## Slide 47: Isopore Membrane Information
Categories | Information
trade name | Isopore
filter color | White
chemistry | Polycarbonate (PC)
water flow rate | Avg. 175 mL/min x cm² (typical results @ 10 psi)
media | Isopore®
wettability | Hydrophilic
porosity | 14.7%
pore size | 1.2 µm
bubble point at 23 °C | 1.0 bar, air with water
thickness | 24 µm
filter diameter (ø) | 25 mm
material size | polycarbonate, Hydrophilic, 1.2 µm, 25 mm, white, plain, 100

## Slide 48: Isopore Membrane Background Information
The Isopore membrane is a polycarbonate, track-etched screen filter recommended for all analyses in which the sample is viewed on the surface of the membrane. The Isopore membrane is composed of polycarbonate film, which has a smooth, glass-like surface for clearer sample observation. The unique manufacturing process of the membrane ensures a precise pore diameter and a consistent pore size for accurate separation of samples by size. Matched-weight filters are not usually required because of low, constant tar and ash weights. Features & Benefits: Membrane structure retains particles on the surface, simplifying counting and analysis

## Slide 49: Jar Test - Filterability Test
Syringe ~ 25 mL from jar (after 5-minutes of settling)
Filter-to-waste 3-5 mL
Filter directly into clean cuvette
Measure turbidity
Note: Take several readings before recording final NTU results. Micro bubbles can adhere to glass causing false NTU readings. To remove bubbles, tilt cuvette up to 90 degrees.

## Slide 50: Contact
Guy Schott, P.E.
State Water Resources Control Board
Division of Drinking Water
Santa Rosa, CA
Go to Stock Solution/Dose calculations/Jar Test Results for tools to download
www.waterboards.ca.gov/drinking_water/programs/districts/mendocino_district.html
Email: Guy Schott - Guy.Schott@waterboards.ca.gov
Office Number: 707-576-2732