## Slide 1: Modesto Irrigation District Ozone Contactor Tracer Study February 26-27, 2019

## Slide 2: Modesto Irrigation District CA5010038 Tracer Study – Ozone Contactor February 26-27, 2019
Tracer Study:
Treatment Plant: Membrane Plant
Reactor: Ozone Contactor
Serpentine: 4 Channels
Volume: 183,000 gallons
Tracer Method: Slug-Dose
Tracer: Fluoride (liquid)
Fluoride Mass Added: ~1,400 grams
Test Flows: 10.2 & 19.9 MGD
Performed by:
Guy Schott, P.E.
CA Division of Drinking Water

## Slide 3: Table of Contents
Summary of Tracer Results
Ozone Reactor Design
Tracer Injection Location
Graphs 1-5: Stations 3-5, 10.2 & 19.9 MGD, Slug-Dose Curves
Purpose of a Tracer Test
Disinfection Exposure Time of Fluid in Vessel for Determining Ct10
Ct10 Value
Baffling Factor (BF)
Tracer Test Method (Slug-Dose)
Method of Analysis and Equipment

## Slide 4: Modesto Irrigation District - Tracer Results #1
Station # | HRT 10.1 MGD | HRT 19.9 MGD | Baffling Factor (BF) t10/HRT 10.2 MGD | Baffling Factor (BF) t10/HRT 19.9 MGD | Tracer % Mass Recovery 10.2 MGD | Tracer % Mass Recovery 19.9 MGD
3 | 12.9 min | - | 0.66 | - | 98 | -
4 | 19.4 min | *9.9 min | 0.77 | *0.58 | 102 | *86
5 | 25.8 min | 13.2 min | 0.76 | 0.72 | 97 | 101
*Recommend to discard this data due to short HRT that may have resulted in inadequate mixing.

## Slide 5: Modesto Irrigation District - Tracer Results #2
Station # | t10 10.2 MGD | t10 19.9 MGD | t50/HRT 10.2 MGD | t50/HRT 19.9 MGD | Morrill Index t90/t10 10.2 MGD | Morrill Index t90/t10 19.9 MGD
3 | 8.5 min | - | 1.38 | - | 1.38 | -
4 | 14.9 min | 7.6 min | 1.26 | 1.17 | 1.26 | 1.17
5 | 19.6 min | 10.0 min | 1.24 | 1.16 | 1.24 | 1.16
Working ozone contactor volume: 138,000 gallons.

## Slide 6: MID Ozone Contactor

## Slide 7: Injection – Slug Dose

## Slide 8: Sample Stations
Three samples stations
(#3, 4 & 5).
Sample frequency were
at 0.5, 1, & 2 minutes.
Station #3
Station #4
Station #5

## Slide 9
Chart: Slug-Dose Curve - Station 3, 10.2 MGD

## Slide 10
Chart: Slug-Dose Curve - Station 4, 10.2 MGD

## Slide 11
Chart: Slug-Dose Curve - Station 4, 19.9 MGD
| 0 | 0 | 0 | 1 | 2 | 2.5 | 3 | 3.5 | 4 | 4.5 | 5 | 5.5 | 6 | 6.5 | 7 | 7.5 | 8 | 8.5 | 9 | 9.5 | 10 | 10.5 | 11 | 11.5 | 12 | 12.5 | 13.5 | 14 | 14.5 | 15 | 15.5 | 16 | 16.5 | 17 | 18 | 19 | 20 | 21 | 22 | 23
 | 0.0014 | 0 | 0 | 0 | 0 | 0.0026 | 0.0016 | 0.0145 | 0.0212 | 0.4812 | 2.3432 | 1.2832 | 3.1332 | 3.2932 | 4.7732 | 3.7632 | 5.0232 | 4.0632 | 3.2332 | 2.4532 | 2.8032 | 2.7932 | 1.3632 | 0.8542 | 0.7702 | 0.6942 | 0.7362 | 0.1692 | 0.1392 | 0.2712 | 0.2232 | 0.0882 | 0.2772 | 0.1432 | 0.0591 | 0.0337 | 0.007 | 0.0049 | 0.0048 | 0.0003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Slide 12
Chart: Slug-Dose Curve - Station 5, 10.2 MGD
| 0 | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 51 | 53 | 55 | 58
 | 0.0006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0102 | 0.153 | 0.845 | 1.098 | 2.308 | 2.798 | 3.098 | 3.378 | 4.478 | 4.818 | 4.418 | 3.898 | 3.698 | 3.258 | 2.368 | 1.988 | 1.798 | 1.228 | 1.248 | 0.88 | 0.616 | 0.421 | 0.431 | 0.288 | 0.248 | 0.213 | 0.104 | 0.106 | 0.073 | 0.0523 | 0.0297 | 0.0216 | 0.0074 | 0.0092 | 0.0099 | 0.0033 | 0.0031 | -0.0009 | 0 | 0 | 0

## Slide 13
Chart: Slug-Dose Curve - Station 5, 19.9 MGD

## Slide 14: Purpose of a Tracer Study
To determine the hydraulic efficiency or disinfectant exposure time of water through one or more reactors.
The addition of known quantities of a nonreactive chemical (tracer) is added in the form of a pulse (slug) or step-input.
The time of travel or disinfectant exposure time through the reactor is related to:
  Flow rate
  Reactor water volume
  Water Depth
  Reactor configuration

## Slide 15: Disinfection Exposure Time of Fluid in Vessel for Determining Ct10
“C” is the disinfectant residual (mg/L) at the point of inactivation compliance.
The disinfection exposure time of water used for Ct10 calculation is the time (t10) it takes for 10 percent of the water entering the reactor to exit the reactor.
To determine this, a marker (nonreactive tracer) is introduced into the water and is monitored leaving the reactor.
Example: 1,000 grams of tracer is slug-dose; t10 is that time when 100 grams of tracer material (10%) has exit the reactor.

## Slide 16: Ct10 Value
- Log inactivation is based on the Delivered Dose, “Ct10”
  “C” is the disinfectant residual (mg/L)
  “t10” is the exposure or contact time (minutes)
  Multiply them:
C • t10 = mg/L • min (delivered dose)
The calculated Ct10 value is looked up in EPA Ct tables to determine the log inactivation based on specific monitoring parameters (pH, disinfectant residual and/or temperature).

## Slide 17: Baffling Factor (BF)
Baffling factor or short-circuiting factor:
  Determined from tracer study or estimated
  BF = t10/ HRT from tracer study
  HRT (hydraulic residence time) = reactor volume divided by reactor flow
Once the BF is determined, then it is applied to the operations of the reactor for determining the disinfectant exposure time.
Example:
  Ozone reactor operating volume: 183,000 gallons
  Exit flow: 7,000 gpm
  BF: 0.70, from tracer study
  Calculated contact or disinfection exposure time:
    183,000 gal ÷ 7,000 gpm × 0.70
    = 18.3 minutes = t10

## Slide 18: Test Method
Slug-Dose or Pulse-Input Method
Adding the entire amount of tracer at the beginning of test. The reactor outlet tracer concentration is monitored for 3-4 HRT to determine mass recovery and the time (t10) it takes for 10% of the tracer mass to exit the reactor.

## Slide 19: Method of Analysis and Equipment
Intellical™ ISEF121 Fluoride (F-) Ion Selective Electrode (ISE)
HQ40d Portable ISE Multi-Parameter Meter
Fluoride Ionic Strength Adjustor (ISA)
Fluoride Standards (0.2/2.0 & 0.5/ 5.0 mg/L)
50 mL graduated cylinder
Finnpipette F2 variable volume pipette, capacity 0.5 - 5 mL
Electrode stirrer stand
50 mL beakers
Stir Bar, Magnetic, Polygon

## Slide 20: Contact
Guy Schott, P.E.
State Water Resources Control Board
Division of Drinking Water
Santa Rosa, CA
Guy.Schott@waterboards.ca.gov
707-576-2732